# NCE LV Switchboard

# Technical Specification

- Manufacturer	NCE - National Concord Engineering

- Designation	LVB for LV Switchboard
	MCC for Motor Control Center
	LMCP for Local Motor Control Panel

- International Standard	ASTA Type Test to IEC 60439-1
	Arc Fault Test to AS3439.1, Appendix EE

- Rated Insulation Voltage for Main Busbar	1000 V

- Rated Operational Voltage	415V \ 380V

- Rated Impulse Withstand Voltage	3.5kV for 1 Minute

- Rated Current	Up to 6300A

- Short Circuit Withstand Strength	80kA for 2500A to 3200A

50kA 3 Sec. for 1600A or Above Busbar
	50kA 1 Sec. for 1250A or Below Busbar

- Degree of Protection	IP31 \ IP42 (Standard Offer)

IP 44 (On request, with Type Tested Certificate)

- Enclosure Framework	2mm Electro-galvanized Sheet Steel Modular Structure

- Coating	Epoxy Powder Coating (Thickness >= 50 Micron)

- Standard Color	RAL 7032 Light Grey

- Busbar Support	Non-hygroscopic GRP

- Copper Busbar	Tinned Copper Busbar to BS1432

- Segregation	Form 4 (LV Switchboards \ MCC)
	Form 3 (LMCP)

- Internal Partition Plate	Aluzinc (Zintec) Sheet Metal

- Cable Entry	Rear Access, Top or Bottom

Front Access (On request)

- Services Conditions	Ambient Temperature up to 40oC
	Relative Humidity up to 100%
	Altitude up to 2000m

Environment up to Pollution Degree 3